## Slide 1
通知
展示板尺寸：1m（宽）×2.40m（高）。
建议海报尺寸：0.95m（宽）×1.40m（高）。
在海报中，您可以以自己的方式编辑文本的字体、颜色、大小和布局。
请将电子海报于2022年10月8日前上传至投稿系统。（海报纸ID：xxx）

## Slide 2
Paper Insulation System Based on New Characteristic Gas
Tel： E-Mail：
I. INTRODUCTION
LIGHTNING strikes are a major cause of outages of transmission lines . It is thus important to improve the performance of lightning protection of transmission lines are calculated by analyzing the lightning overvoltage.
II. EXPERIMENTS
2.1 TEST EQUIPMENT
Tests were carried out in the outdoor experiment field of the National Engineering Laboratory (Kunming) for Ultrahigh-voltage Engineering Technology at an altitude of 2100 m. The dimensions of the field were 197 m × 103 m. Impulse, power frequency and DC test equipment were set up at three within a height range from 45 to 60 m. The distance between sub-conductor lines was 550 mm.
Fig. 1 Diagrams and photographs of the experimental arrangement
V. CONCLUSION
The voltage/time curves of I-string and V-string composite insulators were obtained. The test results show that the voltage/time curves of the I-string and V-string are different even for the same insulation lengths, with the latter being above the former. These results do not agree with the constants of the leader propagation model listed in Table 1.
Configuration | Polarity | k(m2v-2s-1) | E0(kVm-1)
Cap and pin insulators | + | 1.2×10-6 | 520
 | - | 1.3×10-6 | 600
Table 1. Values of k and E0 recommended by CIGRE
IV. THE FORM OF THE FLOW CHART
The template of the flow chart shows below.
III. Results
Figure 2 shows that there were two kinds of lightning impulse discharge paths for the I-string. One had a downward leader and an upward leader, and the other had two downward leaders and two upward leaders. In both cases, the attachment part of the attachment process was located in the middle of the gap. There was 50% probability of generating one leader in discharge in this experiment.
Author's name and organization
Paper ID：XXX
In this paper, the flashover test of the composite insulator used in ±800kV UHVDC transmission lines was carried out in an area of high altitude of 2100 m. U50, the voltage/time curve and constants of the leader propagation model of the I-string and V-string composite insulators were proposed, and the following conclusions were drawn.

## Slide 3
新型配电网的灵活接地方式研究
电话： 邮箱：
Ⅵ. 结论
随着新能源技术的应用，配电网的负荷差异性愈来愈大，而传统配网网络结构中接地点固定的局限将限制配电网的运行灵活性。因此，本文面向未来负荷多变的新能源电网，探讨了一种具有灵活可变接地能力的配网网络架构，其网络拓扑结构的特点是采用隔离变压器对变电站负荷差异比较大的线路进行电气隔离，从而使每条线路都可以根据自身的线路负荷特点灵活选择对应的接地方式。同时，本文以重庆某10 kV变电站为例，通过理论分析和数值仿真，分析了该灵活接地方式的可行性，结果表明采用灵活接地方式的配网网络结构具有更好的线路负荷适应性。
IV. 表格的要求
作者姓名
（作者单位，地址）
Paper ID：XXX
I. 引言
随着新型用电负荷在配电网中的渗透率不断升高，配电网的负荷差异越来越明显，不同的负荷使配电网的接线方式和运行控制都发生了显著变化，给配电网的安全运行带来了更多的挑战。如何改善配电网的网络结构，保障不同负荷的运行环境，增强发生故障时电网的处理能力，确保负荷多变的电网系统内部的故障不会继续扩散，同时增强抵抗不良因素对于电网运行的负面作用，是现在的一个重要研究方向。配电网的接地方式与配电网系统的整体运行方式密切相关，通过灵活改善配电网的接地方式可以来增强配网结构的稳定性。本文提出了一种适用于新型配电网发展的具有灵活可变接地能力的配网网络架构，其网络拓扑结构的特点是采用隔离变压器对变电站负荷差异比较大的线路进行电气隔离，使每条线路都可以根据自身的线路类型特点灵活选择对应的接地方式。
II. 工作原理
灵活接地方式的基本原理是在传统配电网网络拓扑结构的基础上增加一解耦功能模块，将传统配电网构架按负荷要求进行拆分，对电力系统的电源端与负载端进行电气解耦，可以得到两个独立的系统，即母系统和子系统。母系统包括电源端和部分负载端，子系统由被电气隔离的负载端组成。母系统和子系统的中性点接地方式都单独可控。即可以根据出线的线路种类和负荷特点，可以选择最为合适的中性点接地方式。解耦功能模块的最重要的设备是隔离变压器，使用传统隔离变压器进行解耦操作不能达到完全电气隔离的目的，而使用固态隔离变压即可达到目的。
 | 极性 | k(m2v-2s-1) | E0(kVm-1)
绝缘子类型 | + | 1.2×10-6 | 520
 | - | 1.3×10-6 | 600
表 1. CIGRE推荐的k和E0值
V. 仿真分析
由于固态隔离变压器启动需要时间，待系统稳定后再设置故障。在子系统A相设置接地故障，故障设置在0.2s；在母系统中任意选择一条线路设置A相接地故障，故障设置在0.3s，故障电阻统一设为0.1Ω。对母系统与子系统线路电压、电流与故障点电流进行测量，得到图1所示波形。
图1 重庆大学
Fig. 1 Chongqing university
Ⅲ. 实验
灵活接地方式的核心思想在于线路出线处安装解耦功能模块以切断各线路之间的电气联系，从而使每条线路可以工作在最为合适的接地方式下。灵活接地方式的实现方法主要采用固态隔离变压器实现，固态隔离变压器同传统隔离变压器一样具有能量传输和电气隔离的功能，除此之外还可以通过控制调节电能质量、抑制谐波、增强系统稳定性。